상용 순환유동층 보일러 운전 모니터링

선도원, 배달희, 한근희, 조성호

한국에너지기술연구소

대전시유성구 장동 71-2

Commercial Circulating Fluidized Bed Boiler Monitoring

Dowon Shun, Dal-Hee Bae, Keun-Hee Han, Soung-Ho Cho

# Korea Institute of Energy Research

Taejon 305-343, Korea

## INTRODUCTION

Th first commercial circulating fluidized bed combustion(FBC) boiler was introduced to Korea in 19851.  At the present moment around ten units are in operation.  Fuel economy compare to oil boiler is almost doubled in Korean market and the boiler users reports practical gain of energy budget.  The experience of operation has been accumulated during last 15 years, but little operation experiences were reported. The presented work is a summary of the major troubles in CFBC boiler operation.

## OBSERVATIONS

The most chronic and difficult problems in CFBC operation are clinker formation at the various parts of the boiler and erosion of heat exchanger tubes2,3.  Heavy build up of clinkers at the bottom of the combustor4 hinders fluidization and circulation of particles, leading to increase of combustor temperature to beyond the operable limit.  Local erosion can cause tube ruptures and it also leads to sudden boiler shut down.

The characteristics of clinker formation is mainly fuel oriented, the constitution of mineral in coal and sand mixture is the major clue for the explanation. Table 1 shows the analysis of fuel used in Korean industry.   Figure 1 shows the ternary plot of the Al2O3-SiO2-CaO composition of coal ashes and clinkers from commercial boilers.  The crystalline phases of L boiler clinker involved cristoballite, mullite and anorthite.  These clinkers were collected during annual maintenance period.  They were formed at the bottom of the combustor and loop seal.  Upper most square symbol is the analysis of coal mineral and next three are clinkers when operated with limestone, thus increased CaO content.  The lower most square symbol is the clinker when limestone was not used.  The clinker from L boilers seems to grow during long period of operation and it can affect normal operation yet it does not usually leads to emergency shut down.  The clinkers from S boiler are more serious. Shenhwa coal has the composition, which can form low temperature crystallites of anorthite. They were found at the coal feeding chutes where they are connected to return legs of the loop seals.  As soon as they build up they blocked re-circulation line of loop seal and heated up the loop seal over 1273K. The crystalline phases are cristobalite, wollastonite, and anorthite those have lower melting temperature then that of L boiler clinkers.

Erosion is also another factor that can affect boiler performance. The localized erosion can lead to tube rupture and explosion of boiler tubes.  The most serious erosion is the localized water wall erosion located at the water wall and refractory interface.  Often times it is found

Figure 1. Ternary diagram of clinker constituents Figure 2.  Wear of wall tube according to

height above refractory end (Front)

at the convection bank. U bend tubes of superheaters and economizers where flow rate is relatively higher then other area are very much susceptible. The front area of the combustor is susceptible due to the return particle flow from the loop seal.  Upward flow of coals and ashes from the dense bottom converts to down flow at the water wall of the combustor, and those falling particles sweep the wall tube.  Thus, bottom of the water wall and refractory interface where down flow tangentially sweeps is very much weak area.

### Table 1  Analysis of fuels used in CFBC boilers in Korea

|  | Petroleum Coke | Anthracite (Korean) | Tatung | Blair Athol | Shenhwa |
| --- | --- | --- | --- | --- | --- |
| Proximate analysis(Air dry basis) |  |  |  |  |  |
| .Moisture | 5.5 | 3.3 | 8.34 | 5 | 4.84 |
| .Ash | 9.1 | 39.0 | 26.48 | 15 | 32.63 |
| .Volatile matter | 1.6 | 4.0 | 10.37 | 28 | 5.46 |
| .Fixed carbon | 83.8 | 53.7 | 54.81 | 52 | 57.07 |
| Ultimate analysis(Dry basis) |  |  |  |  |  |
| .Carbon | 85.5 | 54.7 | 70.65 | 82 | 73.16 |
| .Hydrogen | 3.6 | 0.3 | 4.74 | 5.1 | 4.11 |
| .Nitrogen | 1.9 | 0.2 | 0.79 | 1.7 | 0.73 |
| .Sulfur | 5.4 | 0.6 | 0.35 | 0.9 | 0.49 |
| High heating value, kcal/kg |  |  |  |  |  |
| .As fired | 8,434 | 4,230 | 6,360 | 6,080 | 6,399 |
| Ash analysis(Dry ash basis) |  |  |  |  |  |
| .SiO2 | 55.0 | 54.5 | 52.24 | 57.4 | 35.82 |
| .Al2O3 | 11.7 | 31.5 | 22.23 | 29.2 | 20.31 |
| .Fe2O3 | 6.6 | 4.7 | 13.57 | 4.4 | 9.63 |
| .CaO | 19.8 | 1.3 | 5.64 | 2.7 | 25.45 |
| .MgO | 2.7 | 1.0 | 1.02 | 0.9 | 1.38 |
| .K2O | 1.00 | 4.0 | 1.71 | 0.7 |  |
| .Na2O | 0.034 | 0.5 | 0.65 | 0.3 | 2.05 |

Figure 2 shows water wall tube thickness measured annual maintenance.  The erosion is severe up to 1000mm above the refractory end.  The damage of 100-200mm above refractory end is most severe so overlay clad is applied to these areas regularly.  But overlay can often converts particle flow and cause more serious damages.  The smoothness of all surfaces including overlay is the key of the maintenance

## DISCUSSION

The clinkers are usually found at the bottom of the combustor, loop seals especially where flow is stagnant (dead zone) thus unburned coal can be burned without moving.  Feeding fuel through return cycle has disadvantage of early ignition of volatile of coal inside the loop seal and that causes the rapid increase of the local temperature.  Since the flow and mixing of the solid is relatively slow in the loop seal area it can easily agglomerate and form clinker.  Feeding highly volatile bituminous coal through loop seal is not proper.  In this case selection of coal which has high fusion temperature can be a way to avoid rapid clinker formation.

Erosion, especially localized water wall erosion is the most serious problem often leads to tube rupture.  Since CFB boiler is operated at high pressure, tube rupture results explosion inside the combustor.  The damages are usually at the lower part of the water wall.  So the users cut out severely damaged part of the water wall and exchange to new materials during regular maintenance.  Also they apply overly clad at the susceptible part.  In this case smoothness of welded part is most important in order to avoid the unexpected change of flow pattern.

## REFERENCES

1. Shun, D. et al., Development of Circulating-Fluidized-Bed Coal Combustion Technology for Co-generation, Korea Institute of Energy Research Kier-973403, Ministry of Trade Industry and Energy, 331pp. (1997).

2. Basu, P., and Fraser, S. A., Circulating Fluidized Bed Boilers, Butterworth-Heinemann, Boston, 349pp. (1991).

3. Colorado-Ute Electric Association, Inc., Nucla Circulating Atmospheric Fluidized Bed Demonstration Project, Final Report, DOE/MC /25-137-3046(DE92001122), Oct, (1991).

4. Lecuyer, I., Leduc, Lefevre, R., and Ausset, P.,"CFBC Ash Characterization: The Case of the Provence 250Unit. Proceedings of the 14th International Conference on Fluidized Bed Combustion, 529-539 (1997).